## Blad1
Strips-Multisensors Data Frame Formats
Data Frame Formats
1. Uplink frames
All Uplink messages on same port can be stacked in same message.
1.1 Port 1
Header
Name | Size [bits] | Range | Description
HistSeqNr | 16 | 0-65535 | Current seqNr of last record in history
1.1.1 Empty report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 0 | Report type
1.1.2 Battery report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 1 | Report type
Batt % | 8 | 0-99 | Battery percentage
1.1.3 Temperature report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 2 | Report type
Temperature | 16 | -400 - 1250 | 0.1 Celcius
1.1.4 Temperature level alarm
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 3 | Report type
Spare | 6 |  | Not used
LowAlarm | 1 | 0, 1 | 0 => Low alarm not active
1 => Low alarm active
HighAlarm | 1 | 0, 1 | 0 => High alarm not active
1 => High alarm active
1.1.5 Average Temperature report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 4 | Report type
Temperature | 16 | -400 - 1250 | 0.1 Celcius
1.1.6 Average Temperature level alarm
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 5 | Report type
Spare | 6 |  | Not used
LowAlarm | 1 | 0, 1 | 0 => Low alarm not active
1 => Low alarm active
HighAlarm | 1 | 0, 1 | 0 => High alarm not active
1 => High alarm active
1.1.7 Relative Humidity Report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 6 | Report type
Temperature | 8 | 0 – 200 | Relative humidity multiplied by 2
1.1.8 Ambient light report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 7 | Report type
Ambient light | 16 | 0 – 65535 | Ambient Light in Lux
1.1.9 Second Ambient light report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 8 | Report type
Ambient light | 16 | 0 – 65535 | Ambient Light in Lux
1.1.10 Door report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 9 | Report type
Door | 8 | 0, 1 | 0 => Door open
1 => Door closed
1.1.11 Door alarm
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 10 | Report type
DoorAlarm | 8 | 0, 1 | 0 => Door closed
1 => Door open, alarm
1.1.12 Tamper switch report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 11 | Report type
Tamper | 8 | 0, 1 | 0 => No magnet on tamper sensor
1 => Magnet on tamper sensor
Note: This is the actual switch state
1.1.13 Tamper alarm
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 12 | Report type
TamperAlarm | 8 | 0, 1 | 0 => No tamper alarm
1 => Tamper alarm active
Note: Tamper Alarm active when door is closed and tamper switch is activated
1.1.14 Flood sensor level report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 13 | Report type
FloodSensor | 8 | 0 - 100 | Flood sensor, 0 – 100%
1.1.15 Flood alarm
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 14 | Report type
FloodAlarm | 8 | 0, 1 | 0 => No alarm
1 => Alarm
1.1.16 Foil alarm
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 15 | Report type
FoilAlarm | 8 | 0, 1 | 0 => Tamper foil attached
1 => Tamper foil removed
1.1.17 User Switch Alarm
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 16 | Report type
UserSwitchAlarm | 8 | 0, 1 | 0 => Switch Off
1 => Switch On
1.1.18 Door Count Report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 17 | Report type
Door Count | 16 | 0-65535 | Number of door open events in specified timeframe
1.1.19 Presence Report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 18 | Report type
Presence | 8 | 0, 1 | 0 => Vacant
1 => Occupied
1.1.20 IR Proximity Report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 19 | Report type
Presence | 16 | 0-65535 | Measured reflection of IR light
1.1.21 IR Low Power Proximity Report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 20 | Report type
Presence | 16 | 0-65535 | Measured reflection of IR light
1.1.22 Close Proximity Report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 21 | Report type
Presence | 8 | 0.1 | 0 => Nothing in close proximity
1 => Something in close proximity
1.1.23 Disinfect Report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 22 | Report type
Disinfect state | 8 | 0-3 | 0 => Dirty
1 => Occupied
2 => Cleaning
3 => Clean
1.1.19 Combined Temperature and Humidity Report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 80 | Report type
Temperature | 16 | -400 - 1250 | 0.1 Celcius
Humidity | 8 | 0 – 200 | Relative humidity multiplied by 2
1.1.20 Combined Average Temperature and Humidity Report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 81 | Report type
Temperature | 16 | -400 - 1250 | 0.1 Celcius
Humidity | 8 | 0 – 200 | Relative humidity multiplied by 2
1.1.21 Combined Temperature and Door Report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 82 | Report type
Temperature | 16 | -400 - 1250 | 0.1 Celcius
Door | 8 | 0, 1 | 0 => Door open
1 => Door closed
1.1.22 Status Report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 110 | Report type
BuildID modified | 1 | 0, 1
BuildID | 31 | 0-4294967295 | ID of the current software build
Status info | 32
1.1.23 Raw Capacitance Flood sensor report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 112 | Report type
CapacitanceValue | 16 | 0 – 65535 | Raw value from capacitance sensor
Note: This is an internal used value, only exposed to diagnose device
1.1.24 Raw Capacitance Pad sensor report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history byffer
1 => This record added to history buffer
Channel | 7 | 113 | Report type
CapacitanceValue | 16 | 0 – 65535 | Raw value from capacitance sensor
Note: This is an internal used value, only exposed to diagnose device
1.1.25 Raw Capacitance End sensor report
Name | Size [bits] | Range | Description
History | 1 | 0, 1 | 0 => Record not added to history buffer
1 => This record added to history buffer
Channel | 7 | 114 | Report type
CapacitanceValue | 16 | 0 – 65535 | Raw value from capacitance sensor
Note: This is an internal used value, only exposed to diagnose device
1.2 Port 2
1.2.1 History item report
Header
Name | Size [bits] | Range | Description
FirstSeqNr | 16 | 0-65535 | Current seqNr of last record in history
Records
Name | Size [bits] | Range | Description
Timestamp | 32 | 0-65535 | Second elapsed since record was created
Record | Depends on record type |  | History record data encoded as in 1.1
Note: “Get history record” response
1.3 Port 11
1.3.1 Configuration Value report
Name | Size [bits] | Range | Description
Command | 8 | 2 | Configuration value
ValueId | 8 | 0-255 | Configuration value Id
Value | 32 | Dependent on value | Value of the configuration setting
Note: “Get configuration value” response
2. Downlink frames
2.1 Port 2
2.1.1 Get history records
Name | Size [bits] | Range | Description
Command | 8 | 1 | Get history record
FirstSeqNr | 16 | 0 – 65535 | First seqNr
LastSeqNr | 16 | 0 – 65535 | Last seqNr
2.2 Port 10
2.2.1 Activate profile
Name | Size [bits] | Range | Description
Command | 8 | 1 | Activate profile
ProfileId | 8 | 0 – 255 | Profile Id
Example: Set to Guard Standard
Transmit 01 04 to device on port 10
2.2.1.1 Profile Id
ProfileName | ProfileId
Default | 0
Comfort Temperature | 1
Comfort Lux | 2
Comfort Average Temperature | 3
Guard Standard | 4
Drip Standard | 5
Presence office (high light quality, slow moving) | 6
Presence public (poor light quality, faster moving) | 7
2.2.1.2 Profile Settings
ProfileName | Settings Altered
Default | All settings set to default values
Comfort Temperature | Base Poll Interval (0x02) => 50
Reports Enabled (0x03) => 00 00 00 04 (TempReport)
History Reports (0x25) => 00 00 00 04 (TempReport)
Comfort Temp & Lux | Base Poll Interval (0x02) => 50
Reports Enabled (0x03) => 00 00 00 84 (TempReport, LuxReport)
History Reports (0x25) => 00 00 00 04 (TempReport)
Comfort Average Temperature | Base Poll Interval (0x02) => 50
Reports Enabled (0x03) => 00 00 00 10 (AvgTempReport)
Avg Temp Time (0x0B) => 86400
History Reports (0x25) => 00 00 00 10 (AvgTempReport)
Guard Standard | Base Poll Interval (0x02) => 15
Reports Enabled (0x03) => 00 00 14 00 (DoorAlarm, TamperAlarm)
History Reports (0x25) => 00 00 14 00 (DoorAlarm, TamperAlarm)
Drip Standard | Base Poll Interval (0x02) => 50
Reports Enabled (0x03) => 00 00 40 00 (FloodAlarm)
History Reports (0x25) => 00 00 40 00 (FloodAlarm)
Presence office (high light quality, slow moving) | Presence treshold => 10
Presence poll interval => 120 s
Presence timeout => 3600 s
Presence public (poor light quality, faster moving) | Presence treshold => 30
Presence poll interval => 60 s
Presence timeout => 1200 s
2.2.2 Unjoin
Name | Size [bits] | Range | Description
Command | 8 | 8 | Unjoin
Rejoin time | 16 | 0 – 65535 | Hours until next Join try
2.3 Port 11
2.3.1 Set Configuration Values
Name | Size [bits] | Range | Description
Command | 8 | 1 | Set configuration values
ValueId | 8 | 0 – 255 | Configuration value Id
Value | 32 | Dependent on value | Value to be set
Note: ValueId and Value can be repeated to set multiple values
2.3.2 Get Configuration Values
Name | Size [bits] | Range | Description
Command | 8 | 2 | Get configuration values
ValueId | 8 | 0 – 255 | Configuration value Id
Note: ValueId can be repeated to fetch multiple values
2.3.2.1 Configuration Value Id
ValueId [hex] | Range | Unit | Default Value | Description
2 | 10 - INT16_MAX | 0.1 Seconds | 15 | Base poll interval
0x02
3 | Report Bitfield | Bitfield | 0x00000A00 | Enabled sensors bitfield
0x03 |  |  | (DoorReport, TamperReport)
4 | 0, 10 - INT32_MAX | Seconds | 120 | Temperature poll interval
0x04
5 | 0, 100 – 160000 | milliCelcius | 2000 | Temperature send Immediately threshold
0x05
6 | 0, 100 – 160000 | milliCelcius | 1000 | Temperature send threshold, throttled
0x06
7 | 60 – INT32_MAX | Seconds | 3600 | Temperature Throttled Time
0x07
8 | -40000 – 120000 | milliCelcius | -40000 | Temperature Low Alarm Level
0x08
9 | -40000 – 120000 | milliCelcius | 120000 | Temperature High Alarm Level
0x09
10 | 100 – 160000 | milliCelcius | 1000 | Temperature Alarm Hysteresis
0x0a
11 | 0, 10 – INT32_MAX | Seconds | 86400 | Average Temperature Time
0x0b
12 | -40000 – 120000 | milliCelcius | -40000 | Average Min Temperature
0x0c
13 | 0, 100 – 160000 | milliCelcius | 0 | Average Temperature send Immediately threshold
0x0d
14 | -40000 – 120000 | milliCelcius | -40000 | Average Temperature Low Alarm Level
0x0e
15 | -40000 – 120000 | milliCelcius | 120000 | Average Temperature High Alarm Level
0x0f
16 | 100 – 160000 | milliCelcius | 1000 | Average Temperature Alarm Hysteresis
0x10
17 | 0, 10 – INT32_MAX | Seconds | 0 | Humidity Poll Interval
0x11
18 | 0, 1 – 100 | % | 4 | Humidity Send Threshold
0x12
19 | 0, 10 – INT32_MAX | Seconds | 60 | Ambient Light Poll Interval
0x13
20 | 0-65535 | Lux | 0 | Ambient Light send high level
0x14
21 | 0-65535 | Lux | 0 | Ambient Light send low level
0x15
22 | 0-65535 | Lux | 0 | Ambient Light send high level2
0x16
23 | 0-65535 | Lux | 0 | Ambient Light send low level2
0x17
24 | 0, 1 – INT32_MAX | Seconds | 30 | Flood sensor poll interval
0x18
25 | 0 – INT16_MAX | CapacitanceValue | 400 | Flood sensor 0% Capacitance value
0x19
26 | 0 – INT16_MAX | CapacitanceValue | 1600 | Flood sensor 100% Capacitance value
0x1A
27 | 0, 10 – INT32_MAX | Seconds | 0 | Flood report interval
0x1B
28 | 0 – 100 | % | 10 | Flood Alarm Threshold
0x1C
29 | 0 – 100 | % units | 4 | Flood Alarm Hysteresis
0x1D
30 | 0 – INT16_MAX | Raw capacitance value | 1450 | Tamper foil treshold
0x1E
31 | 0, 1 – INT32_MAX | Seconds | 0 | Flood sensor raw value report interval
0x1F
32 | 0, 1 – INT32_MAX | Seconds | 0 | Pad sensor raw value report interval
0x20
33 | 0, 1 – INT32_MAX | Seconds | 0 | End sensor raw value report interval
0x21
34 | Report Bitfield | Bitfield | 0 | Combined sensors1
0x22
35 | Report Bitfield | Bitfield | 0 | Combined sensors2
0x23
36 | Report Bitfield | Bitfield | 0 | Combined sensors3
0x24
37 | Report Bitfield | Bitfield | 0 | History reports
0x25
38 | 0, 60 – INT32_MAX | Minutes | 1440 | Demo state try join interval
0x26
39 | 0 – 1000 | % | 400 | Lux plastic housing compensation
0x27
40 | 0-INT16_MAX |  | 0x00 00 01 FF | LoRa data rate
0x28 |  |  |  | Byte 1 (MSB): Not used
Byte 2: Not used
Byte 3: 0-15 for lowest data rate to be used with ADR
Byte 4 (LSB): 0-15 for DR_0 – DR_15 or 0xFF to enable ADR
41 | 0-2 | LED Level | 2 | LED Level
0x29 |  |  |  | 0 => almost no indications, 2 => Indicate everything
42 | 0-INT32_MAX | Hours | 24 | Status report interval
0x2A
43 | 1-INT32_MAX | Hours | 168 | Resend Reset Time
0x2B |  |  |  | Time in resend mode before reboot
44 | 0-INT32_MAX | Lux | 25 | Lux Low Cutoff
0x2C |  |  |  | Only report lux values once below this level
45 | 0-INT32_MAX | Seconds | 3600 | Door Count Report Interval
0x2D
46 | 0-INT32_MAX | Seconds | 600 | IR Proximity Report Interval
0x2E
47 | 0-INT32_MAX | Seconds | 120 | Presence poll interval
0x2F
48 | 0-INT32_MAX | IR reflection noise floor | Presence R1, R2: 10, R3: 30 | Presence treshold
0x40
49 | 0-INT32_MAX | Seconds | 3600 | Presence timeout
0x41
2.3.2.2 Report Bitfields values
BitValue | Name
0x00000001 | Empty Report
0x00000002 | BatteryReport
0x00000004 | TempReport
0x00000008 | TempAlarm
0x00000010 | AverageTempReport
0x00000020 | AverageTempAlarm
0x00000040 | HumidityReport
0x00000080 | LuxReport
0x00000100 | LuxReport2
0x00000200 | DoorReport
0x00000400 | DoorAlarm
0x00000800 | TamperReport
0x00001000 | TamperAlarm
0x00002000 | FloodReport
0x00004000 | FloodAlarm
0x00008000 | FoilAlarm
0x00010000 | TempHumReport
0x00020000 | AvgTempHumReport
0x00040000 | TempDoorReport
0x00080000 | CapacitanceFloodReport
0x00100000 | CapacitancePadReport
0x00200000 | CapacitanceEndReport
0x00400000 | UserSwitchAlarm
0x00800000 | DoorCountReport
0x01000000 | PresenceReport
0x02000000 | IRProximityReport
0x04000000 | IRLowPowerProximityReport
0x08000000 | IRCloseProximityAlarm
0x10000000 | DisinfectAlarm